OPA8 (Manchester, PA) – Power, Estimated Timelines and Deliverables

Date: March 27, 2026

Project: OPA8 (Manchester, PA) – Manchester Commerce Center Building 2

1. Purpose

This memo summarizes the current status of power for Building 2, outlines requirements and options for temporary power, and gathers information necessary for establishing comprehensive timelines and deliverables to ensure timely progress.

2. Baseline Electrical Condition

The building’s installed electrical gear supports equipment loads up to 8000A. However, First Energy (FE) has restricted service to a secondary supply of approximately 2,000 kVA / 2,400A at 480V, 3-phase, while the substation is under construction. Temporary power may supplement this supply if needed. For additional information on temporary power requirements and options, see section 4 below.

3. Estimated timeline to transmission power / Substation completion (High-Level)

Critical path is driven by the 26-month FE projection based on general language within the 12/20/25 Design Load Study that specifically states the following:  "FE anticipates that the proposed work can be completed in approximately 26 months after the execution of a service contract for the project.  This includes time for engineering, material delivery, and construction.  Customer acknowledges and agrees that this is not FE’s commitment, nor is it a guarantee of, any specific in-service date; instead"

This estimate includes conservative durations for obtaining easements and addressing wetland impacts; neither is a concern as NP owns the property and there are no environmental constraints. We anticipate a reduced timeline once a FE Project Manager (PM) is assigned for procurement and scheduling of the project-specific scope.

NPD scope of work for the substation build out is currently projected to be completed by Q1 of 2027.

Next steps for progression of Met-ed Controlled scope:

    - Execute CSA (once received) current estimated delivery 3/27/26

    - Met‑Ed issues invoice: current ETA to immediately follow delivery CSA

    - NPD makes payment (once CSA is reviewed and approved for accuracy)

    - Payment triggers Met‑Ed PM assignment

    - FE PM engages engineering; confirm long-lead equipment needs (switches, SCADA switch components, metering coordination, etc.) and release procurement

    - Met‑Ed to provide a more detailed delivery schedule once PM/engineering are engaged (more precise than the blanket 26‑month estimate)

4. Temporary Power (Interim Period – Until Transmission Service is Delivered)

Temporary power can be provided via generator(s) for power needs in excess of the current available load, until the full dedicated load is delivered.

Temporary power cannot exceed the installed infrastructure limits of the installed equipment and gear stated above unless additional equipment is designed installed as part of the tenant improvements.

See below for requirements.

Summary – Deliverables by Party

The following list consolidates our interpretation of deliverables/actions required to advance the different moving aspects of this project.

Amazon Deliverables

- NorthPoint needs estimated timeline(s) for the following: (please reorder to align with how approvals will flow through Amazon internally so we can expand with our deliverables for a full picture schedule.)

  - CAR Budget approval

  - CRA Budget approval

  - Finalize site design for NPDES minor mod

  - Fencing and signage plans and submittals for preparation of Special Exception

- The following items are required from Amazon to determine 1) if temp power is necessary and 2) the costs/timeline for temporary generation.

- Detailed load sheets, identifying:

  - Panel-by-panel connected load and expected usage/duty cycle for each major equipment category; include proposed demand assumptions where available.

  - Equipment demand

  - Daily usage characteristics

- Updated electrical one-line and plan with updated panel locations for determining placement of temporary power.

- Power ramp-up schedule, identifying:

  - Day-one operational load

  - Milestones for phased increases through full operations

  - Target in-service / commissioning milestones: dates tied to commissioning, energization needs, and operational cutovers so interim power can be matched to the schedule.

If available provide utility bills/usage data from comparable facilities (if available) to support load factor and demand assumptions.

Notes: Temporary power is limited by installed infrastructure (switchgear/panels/gear). The above inputs are required to confirm feasibility and to avoid exceeding equipment limits or what might be needed above and beyond existing equipment until the substation comes online.

NorthPoint Development (NPD) Deliverables

Lease revision with latest requested format (Amazon performed TIs with NPD assistance with select Entitlements) – Attached.

Provide base one-line diagram for Amazon markups and coordinate review of proposed tie-in locations.  – Attached

Draft CRA – included for review and comment. Attached

Execute the CSA upon receipt from FE and process payment of Met-Ed invoice to trigger project assignment and engineering engagement.

Contingent upon CSA review and accuracy.

Outline temporary power options and estimated cost once Amazon provides information outlined above.

Met-Ed / FirstEnergy Deliverables

Issue Contract Service Agreement (CSA)

Anticipated 3/27/26

Issue final invoice to NPD

Assign Met-Ed Project Manager and engage internal engineering teams after CSA execution and payment steps are complete.

Provide refined schedule for Met-Ed scope after PM/engineering engagement.

Estimated timeline TBD by Met-ed

Deliver Met-Ed transmission connection scope (tap/line extension, SCADA-controlled switches, relay adjustments, metering integration).